# Rectifier Validation Report

## 1. Objective

To evaluate the performance, efficiency and thermal behavior of the rectifier under specified operating conditions.

## 2. Test Setup

The rectifier DUT was tested using the validation test setup. Electrical parameters such as voltage, current, power and temperature were monitored and recorded throughout the test duration.

## 3. Validation Summary

Maximum Efficiency : 97.96%

Minimum Efficiency : 94.76%

Average Efficiency : 95.37%

Maximum Output Power : 27.03 kW

Average Output Power : 25.42 kW

Maximum Temperature : 39.80 °C

Average Temperature : 38.57 °C

Average Output Voltage : 698.82 V

## 4. Test Evaluation

Efficiency Result : PASS

Temperature Result : PASS

Overall Result : PASS

## 5. Observations

The rectifier achieved an average efficiency of 95.37% which meets the acceptance criteria.

Thermal performance was satisfactory with a maximum temperature of 39.80 °C.

The maximum output power delivered during the test was 27.03 kW.

The average output voltage during the test was 698.82 V.

## 6. Graphs

Efficiency Graph

Output Voltage Graph

Temperature Graph

Output Power Graph

## 7. Conclusion

The rectifier successfully passed the validation test. The average efficiency was 95.37% and the maximum temperature remained within acceptable limits. The DUT is considered suitable for operation under the tested conditions.